Device Information

| Chiller Number | 4998J59038 |
| --- | --- |
| Location Name | 811 10th Ave-811 10th Ave |
| Location City | New York |
| Postal Code | 10019-5042 |
| Site Address | 811 10th Ave |
| Time-zone | America/New_York |
| Year of Manufacturing (Age) | 1998(26 Years) |
| Model Number | 19XR-6765465DFS64- |
| Report Duration | 2023-01-06 ~ 2023-08-15 |
| Chiller Run Hours | 53,469 |

Summary

As part of Carrier’s connected chiller program our command center experts continuously monitor performance and health of your chiller and its major components to provide real time feedback and less operational disruption.

Your chiller serial number 4998J59038 was evaluated for Chiller Replacement Analysis. Further Analysis is performed from the real time data from 2023-01-06 to 2023-08-15. The design efficiency of current chiller is 0 kW/T. The overall efficiency of this chiller is 0.53 kW/T. Replacing this with a Carrier Aqua Series Water Cooled Chillers can improve the overall efficiency to 0.41 kW/T. This replacement can improve the chiller efficiency by 23%. The chiller is running at low loads (<60% RLA) for 50% during the analysis period and this replacement can enhance design integrated part-load values (IPLV) to as low as 0.37 kW/T.

Chiller Replacement Benefits:

- Improved Efficiency

- Reduces operating expenses.

- Easy to maintain.

- Quiet operation

- Reliable operation

- Environmentally sustainable refrigerant

- ASHRAE 90.1 compliant

- High-efficiency optimization

- Diagnostic controls

Based on the performance of the chiller operation versus measured parameters, Carrier recommends further evaluation of the Chiller Replacement by our certified technician. This will ensure optimal performance of the Chiller.

Alarm/Setpoint Analysis

There are no alarms during this period.

The analysis result show that setpoint not meeting 1% of time.

Comments

The Average Cooler supply water temperature is between 43.9 to 44.6 (°F) and the average Condenser entering water temperature is between 70.2 to 78.4 (°F).

| Chiller Sub System Health |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Chiller # |  | Condenser Health (Good/Stage of Degradation) | Evaporator Health (Good/Stage of Degradation) |  | Compressor Performance (Good/Stage of Degradation) | Ref leak (Good/Stage of Degradation) | Condenser Water Flow Issue (Yes/No) | Evaporator Water Flow Issue (Yes/No) |
| 4998J59038 |  |  |  |  |  |  |  |  |
| S1 | No action required |  |  |
| S2 | Plan to clean/fix |  |  |
| S3 | Clean/Fix immediately |  |  |
| S4 | - |  |  |

Summary

| Energy Efficiency Improve | 23% |
| --- | --- |
| Energy Savings | 137,469 kWh |
| Energy Savings/per year | 227,042 kWh |
| Investment pay-back period | 10.3 Years |