Device Information

| Chiller Number | 5200Q64908 |
| --- | --- |
| Location Name | SUMIKA ELECTRONIC MATERIALS INC |
| Location City | Phoenix |
| Postal Code | 85034 |
| Site Address | 3832 E Watkins St |
| Time-zone | America/Phoenix |
| Year of Manufacturing (Age) | 2000(24 Years) |
| Model Number | 19XRV5051446DDH464 |
| Report Duration | 2022-09-12 ~ 2024-01-02 |
| Chiller Run Hours | 79,334 |

Summary

As part of Carrier’s connected chiller program our command center experts continuously monitor performance and health of your chiller and its major components to provide real time feedback and less operational disruption.

Your chiller serial number 5200Q64908 was evaluated for Chiller Replacement Analysis. Further Analysis is performed from the real time data from 2022-09-12 to 2024-01-02. The design efficiency of current chiller is 0.6 kW/T. The overall efficiency of this chiller is 0.75 kW/T. Replacing this with a Carrier Aqua Series Water Cooled Chillers can improve the overall efficiency to 0.48 kW/T. This replacement can improve the chiller efficiency by 36%. The chiller is running at low loads (<60% RLA) for 91% during the analysis period and this replacement can enhance design integrated part-load values (IPLV) to as low as 0.39 kW/T.

Chiller Replacement Benefits:

- Improved Efficiency

- Reduces operating expenses.

- Easy to maintain.

- Quiet operation

- Reliable operation

- Environmentally sustainable refrigerant

- ASHRAE 90.1 compliant

- High-efficiency optimization

- Diagnostic controls

Based on the performance of the chiller operation versus measured parameters, Carrier recommends further evaluation of the Chiller Replacement by our certified technician. This will ensure optimal performance of the Chiller.

Alarm/Setpoint Analysis

The analysis result show that setpoint not meeting 0% of time.

Comments

The Average Cooler supply water temperature is between 42.6 to 43.5 (°F) and the average Condenser entering water temperature is between 72.5 to 80.4 (°F).

| Chiller Sub System Health |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Chiller # |  | Condenser Health (Good/Stage of Degradation) | Evaporator Health (Good/Stage of Degradation) |  | Compressor Performance (Good/Stage of Degradation) | Ref leak (Good/Stage of Degradation) | Condenser Water Flow Issue (Yes/No) | Evaporator Water Flow Issue (Yes/No) |
| 5200Q64908 |  |  |  |  |  |  |  |  |
| S1 | No action required |  |  |
| S2 | Plan to clean/fix |  |  |
| S3 | Clean/Fix immediately |  |  |
| S4 | - |  |  |

Summary

| Energy Efficiency Improve | 36% |
| --- | --- |
| Energy Savings | 319,070 kWh |
| Energy Savings/per year | 244,152 kWh |
| Investment pay-back period | 6.7 Years |